## 1.Change History
Mazda_Gen7: SRS_WIM_MazdaDHSWarningIndicatorMgt
Change History
Document Version | Author | Description | SRS baseline
1.1 | Ha Quang Hien (RBVH/ESS2) | First release Matrix for DHSWarningLamp | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.4
1.2 | Ha Quang Hien (RBVH/ESS2) | Rework after finding reviews on Ptedt00863376 | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.4
1.3 | Ha Quang Hien (RBVH/ESS2) | Adding: - Sheet 5: DHSWarningLampNotOperationFault - Sheet 6: MisMatch Fault sheet | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.4
1.4 | Ha Quang Hien (RBVH/ESS2) | Update based on Ptedt00868056 | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.7
1.5 | Ho Thi Be (RBVH/ESS2) | Update based on Ptedt00868084 & | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.7
1.6 | Luu Duc Trong Nhan (RBVH/ESS2) | Update TS ID for Sheet 5 & 6 | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.7
1.7 | Ha Quang Hien (RBVH/ESS2) | Update TS ID to Sheet 3 & 4 Update Open Fault to Sheet 3 & 4 | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.7
1.8 | Ha Quang Hien (RBVH/ESS2) | Update Fault to Short2Gnd (for Init Fault) Add remark to 3.InitializationAndSteadySt / cell M32 | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.7
1.9 | Ha Quang Hien (RBVH/ESS2) | Remove rb_psem_Short2GndPCSC_flt in 3.InitializationAndSteadySt/ cell K67 due to no PCSC device. | SRS_WIM_MazdaDHSWarningIndicatorMgt 0.7

## 2.Summary
Mazda AB12_DHSWLIndicatorMgt SRTP Matrix
<Purpose>
The document is created for DHS Warning Lamp Indicator Management SRTP to test all possible and robust test scenarios
Test scenarios covered under each section is listed below
Part 1
SRTP Section | DESCRIPTION | SHEET
Initialization | To check behaviour of DHSWL Mgt module at the time of Initialization and prove out time To check the Mazda plant mode | 3.Initialization and Steady State
Power Down | To check the DHSWL value when the Autarky is appeared | 4. Power down
Power Down | Additional scenarios for the WIM in power down mode in table c and table d | 4. Power down
Part 2
SRTP Section | DESCRIPTION | SHEET
DHS Warning Lamp Not Operation Fault | Check DSHWL Not Operation Fault in different conditions. | 5. NotOperationFault
MisMatch Fault | Check DSHWL MisMatch Fault in different conditions. | 6. MisMatch Fault
ECU mode
DEM
Mazda Plant mode
System config
Mazda Warning Indicator Management
HEC
PSEM
Bus-off condition, …
Faulty condition, …
CAN bus
DHSWL

## System WarningIndicator_Csample (hidden)
Definition of system WL Indicator
1. Through CAN: Message _RCMStatusMessage (CAN Id 0x340); RILReq Signal
- Value of CAN signal in different cases
Worst case of delay time from the fault detection to sending the first message successfully into CAN Line is 120ms
SRS ID | Fault with 'WL on' condition | ECU mode | IGN time | Output (CAN Id 0x340_RILReq) | SRTP ID | Remarks
SRS_WIM_316 | Qualified | Normal | since Fault qualified -> 120 ms | Updated from $0 -> $3 |  | No set => Confirm (C sample)
SRS_WIM_295 SRS_WIM_242 | --------------- | Plant | 0 -> Later | Blinking 5Hz $2 (Value blinks every 200 ms) |  | C sample

## 3.InitializationAndSteadySt
Initialization and Steady State
Confirmation point:
Check DSHWL Request Signal state in Proveout time & Steady state with different condition.
Conditions considered:
1. ITM mode
2. Mazda Plant Mode
3. Abnormal Voltage
4. Faulty Condition
Voltage Dependency:
1. Set Voltage as 12V
2. Set Abnormal Voltage
Testing Technique:
1. Equivalence partitioning
a) To check transmitted value of DHSWL after Proveout time while ECU still is on ITM mode
| SRS ID | Precondition |  | Input |  | Output - DHSWL (CAN Id 0x340_ DHS_RILReq) | Test Strategy | SRTP ID | Remarks
|  | ECU Mode | Voltage condition | Condition | IGN ON and wait (s)
| SRS_DHSWL_135 | ITM | 12V (Normal Voltage) | ITM expands | 8s(+/-0.3) | 1 | Equivalence partitioning | TS_DHSWL_188 | No execute anymore, due to System not able to expand ITM time
|  | ITM | 7V (Low Voltage) |  | 8s(+/-0.3) | 1 | Equivalence partitioning | TS_DHSWL_189
|  | ITM | 20V (High Voltage) |  | 8s(+/-0.3) | 1 | Equivalence partitioning | TS_DHSWL_236
| SRS_DHSWL_169 | IDLE | 12V (Normal Voltage) | ITM not finish normally | 8s(+/-0.3) | 1 | Equivalence partitioning | TS_DHSWL_691
|  | IDLE | 7V (Low Voltage) |  | 8s(+/-0.3) | 1 | Equivalence partitioning | TS_DHSWL_692
|  | IDLE | 20V (High Voltage) |  | 8s(+/-0.3) | 1 | Equivalence partitioning | TS_DHSWL_693
b) To check the transmitted value of DHSWL in Proveout Time & Steady State with affected of fault and voltage condition
| SRS ID | Precondition |  | Input |  | Output - DHSWL (CAN Id 0x340_ DHS_RILReq) | Test Strategy | SRTP ID | Remarks
|  | Voltage condition | ECU mode | Fault condition | IGN ON and wait (s)
| SRS_DHSWL_42 | 12 V (Normal Voltage) | ITM | No fault/ Fault DHSWL off | 0s -> 6s +/- 0.15s | 1 | Equivalence partitioning | TS_WIM_275
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 0
| SRS_DHSWL_42 |  | ITM | Fault on DHSWL qualified within 0->6s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_459 | rb_psem_Short2GndPCS1D_flt
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 3
| SRS_DHSWL_42 |  | ITM | Create Fault Condition on DHSWL and remove the condition before Fault qualified within 0->6s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_476 | rb_psem_Short2GndPCS1P_flt, Finding 61280918
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 0
| SRS_DHSWL_42 |  | ITM | Fault on DHSWL qualified within 6s->8s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_455 | rb_psem_Short2GndPCS2D_flt
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 3
| SRS_DHSWL_156 |  | Normal | Create Bus-off condition and remove the condition | 8s +/- 0.3s | Bus-off: CAN stop transmission |  | TS_WIM_483
Remove Bus-off: $0
| SRS_DHSWL_156 |  | Normal | Create Fault Condition & Create Bus-off condition and remove Bus-off | 8s +/- 0.3s | Bus-off: CAN stop transmission |  | TS_WIM_482 | rb_psem_Short2GndPCS2P_flt
Remove Bus-off: $3
| SRS_DHSWL_42 | 7 V (Low Voltage) | ITM | No fault/ Fault DHSWL off | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_456
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 0
| SRS_DHSWL_42 |  | ITM | Fault on DHSWL qualified within 0->6s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_457 | rb_psem_Short2GndPCS3D_flt
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 3
| SRS_DHSWL_42 |  | ITM | Fault on DHSWL qualified within 6s->8s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_458 | rb_psem_Short2GndPCS3P_flt
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 3
| SRS_DHSWL_42 | 20V (High Voltage) | ITM | No fault/ Fault DHSWL off | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_419
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 0
| SRS_DHSWL_42 |  | ITM | Fault on DHSWL qualified within 0->6s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_453 | rb_psem_Short2GndPCSC_flt rb_psem_Short2GndPCS1D_flt
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 3
| SRS_DHSWL_42 |  | ITM | Fault on DHSWL qualified within 6s->8s from IGN ON. | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_454 | rb_psem_Short2GndPCS1D_flt
| SRS_DHSWL_136 |  | ITM |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156 |  | Normal |  | 8s +/- 0.3s | 3
c) To check the transmitted value of DHSWL with affected of Plant Mode and voltage condition
| SRS ID | Precondition |  | Input |  |  | Output - DHSWL (CAN Id 0x340_ DHS_RILReq) | Test Strategy | SRTP ID | Remarks
|  | Voltage condition | ECU mode | Condition 1 | Condition 2 | IGN ON and wait (s)
| SRS_DHSWL_42, 125 | 12 V (Normal Voltage) | ITM | No fault/ Fault DHSWL off |  | 0s -> 6s +/- 0.15s | 1 | Equivalence partitioning | TS_WIM_503, 517
| SRS_DHSWL_136, 125 |  | ITM |  | Mazda plant mode | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 |  | ITM | Fault on DHSWL qualified within 0->6s from IGN ON. |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_504, 518 | rb_psem_Short2GndPCS1D_flt
| SRS_DHSWL_136, 125 |  | ITM |  |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 |  | ITM | Fault on DHSWL qualified within 6s->8s from IGN ON. |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_505, 519 | rb_psem_Short2GndPCS1P_flt
| SRS_DHSWL_136, 125 |  | ITM |  |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 | 7 V (Low Voltage) | ITM | No fault/ Fault DHSWL off |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_506, 520
| SRS_DHSWL_136, 125 |  | ITM |  | Mazda plant mode | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 |  | ITM | Fault on DHSWL qualified within 0->6s from IGN ON. |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_507, 521 | rb_psem_Short2GndPCS2D_flt
| SRS_DHSWL_136, 125 |  | ITM |  |  | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 |  | ITM | Fault on DHSWL qualified within 6s->8s from IGN ON. |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_508, 522 | rb_psem_Short2GndPCS2P_flt
| SRS_DHSWL_136, 125 |  | ITM |  |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 | 20V (High Voltage) | ITM | No fault/ Fault DHSWL off |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_509, 523
| SRS_DHSWL_136, 125 |  | ITM |  | Mazda plant mode | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 |  | ITM | Fault on DHSWL qualified within 0->6s from IGN ON. |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_510, 524 | rb_psem_Short2GndPCS3D_flt
| SRS_DHSWL_136, 125 |  | ITM |  |  | 6s+/-0.15s -> 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 125 |  | ITM | Fault on DHSWL qualified within 6s->8s from IGN ON. |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_511, 525 | rb_psem_Short2GndPCS3P_flt
| SRS_DHSWL_136, 125 |  | ITM |  |  | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156, 125 |  | Normal |  |  | 8s +/- 0.3s | 2
| SRS_DHSWL_42, 127 | 12 V | ITM | No fault/ Fault DHSWL off |  | 0s -> 6s +/- 0.15s | 1 |  | TS_WIM_527, 526
| SRS_DHSWL_136, 127 | (Normal Voltage) | ITM |  | Bosch plant mode | 6s+/-0.15s - 8s +/- 0.15s | 0
| SRS_DHSWL_156, 127 |  | Normal |  |  | 8s +/- 0.3s | 3
b) To check the transmitted value of DHSWL in with Disqualification condition
| SRS_ID | Precondition |  | Input | Output |  |  | Input | Output | Input | Output | Input | Output | Input | Output | Test Strategy | SRTP ID | Remarks
|  | ECU mode | Voltage condition | Create Faulty condition | DHS_RILReq within 6s proveout time | DHS_RILReq from 6s - 8s | RILReq after 8s | Reset ECU 5 times | DHS_RILReq after 8s for 5 times | Remove faulty condition | DHS_RILReq after 8s | Reset ECU | DHS_RILReq after 8s | Reset ECU 5 times | DHS_RILReq after 8s
| SRS_DHSWL_42 | Normal | Normal | Fault on DHSWL qualified within 0->6s | 1 | 0 | 3 | Yes | 3 | Yes | 0 | Yes | 0 | Yes | 0 | Equivalence partitioning | TS_WIM_534 | rb_psem_Short2GndPCS1D_flt
| SRS_DHSWL_136 |  |  | Fault on DHSWL qualified within 6->8s | [11 empty] | Equivalence partitioning | TS_WIM_535 | rb_psem_Short2GndPCS1P_flt
| SRS_DHSWL_42 |  |  | 2 Faults on DHSWL qualified within 0-6s | [5 empty] | Yes: Disqualify just 1 Fault | 3 |  | 3 |  | 3 | Equivalence partitioning | TS_WIM_542 | rb_psem_Short2GndPCS2D_flt 'rb_psem_Short2GndPCS2P_flt
e) To check the transmitted value of DHSWL with AB Faults:
| SRS_ID | Precondition |  | Input | Output |  |  | Input | Output | Input | Output | Input | Output | Input | Output | Test Strategy | SRTP ID | Remarks
|  | ECU mode | Voltage condition | Create Faulty condition | DHS_RILReq within 6s proveout time | DHS_RILReq from 6s - 8s | RILReq after 8s | Reset ECU 5 times | DHS_RILReq after 8s for 5 times | Remove faulty condition | DHS_RILReq | Reset ECU | DHS_RILReq after 8s | Reset ECU 5 times | DHS_RILReq after 8s
| SRS_DHSWL_42, 136, 156 | Normal | Normal | Cyclic fault: AB1FD Squib Open | 1 | 0 | 0 | Yes | 0 | Yes | 0 | Yes | 0 | Yes | 0 | Equivalence partitioning | TS_WIM_548
| SRS_DHSWL_42, 136, 156 |  |  | Init fault: rb_sqm_CrosscouplingAB1FD_flt | 1 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | Equivalence partitioning | TS_WIM_551
| SRS_DHSWL_42, 136, 156 |  |  | Internal Fault: rb_csem_InitGroup flt | 1 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | Equivalence partitioning | TS_WIM_552
| SRS_DHSWL_42, 136, 156 |  |  | Crash Fault | 1 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | Equivalence partitioning | TS_WIM_553
| SRS_DHSWL_42, 136, 156 |  |  | CAN fault: HEC lost communication | 1 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | Equivalence partitioning | TS_WIM_554
| SRS_DHSWL_42, 136, 156 |  |  | Fault with Lamp Off: VDS | 1 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | Equivalence partitioning | TS_WIM_555
| SRS_DHSWL_42, 136, 156 |  |  | Combination of faults with different WL status with 'Never dequalified fault' | 1 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | Equivalence partitioning | TS_WIM_556
f) To check the timing between 2 message
| SRS_ID | Precondition |  | Input |  | Output - DHSWL (CAN Id 0x340_ DHS_RILReq) | Input | Output - DHSWL (CAN Id 0x340_ DHS_RILReq) | Test Strategy | SRTP ID | Remarks
|  | Voltage condition | ECU mode | Fault condition | IGN ON and wait (s) |  | Condition
| SRS_DHSWL_160 | 12V (Normal Voltage) | Normal | rb_psem_Short2GndPCS2D_flt qualified after 8s +/-0.3s from IGN ON. | 8s +/- 0.3s | $0 -> $3 within 120ms from Fault Qualified | Remove rb_psem_Short2GndPCS2D_flt condition | $3 -> $0 within 120ms from Fault Disqualified | Equivalence partitioning | TS_WIM_563 | - Ptedt00864899 - 120ms from Fault Disqualified (not from Fault Condition removed)

## 4.Power Down
Power Down
Confirmation point:
Check DSHWL Request Signal state in Autarky mode
Conditions considered:
1. Autarky mode
2. Abnormal Voltage
3. Faulty Condition
Voltage Dependency:
1. Set Voltage as 12V
2. Set Abnormal Voltage
Testing Technique:
1. Equivalence partitioning
a) To check the behaviour of the DHSWL when power down is appeared during ECU steady state
| SRS ID | Precondition |  | Input |  |  | Output | Test Strategy | SRTP ID | Remarks
|  | ECU mode | Voltage Condition | Fault Detection | Power Cut off | Timing | DHS_RILReq
| SRS_DHSWL_157 | Normal mode | Normal Voltage (12V) | No fault | Yes (After 8.3 s from IGN ON) | Autarky Time (450 ms from Power Cut off) | 0 | Equivalence partitioning | TS_DHSWL_576
|  |  | Low Voltage (7V) | Fault Qualified (Low Voltage Fault) | Yes (After 8.3 s from IGN ON) | Autarky Time (450 ms from Power Cut off) | 0 | Equivalence partitioning | TS_DHSWL_577
|  |  | High Voltage (16.5 V) | Fault Qualified (High Voltage Fault) | Yes (After 8.3 s from IGN ON) | Autarky Time (450 ms from Power Cut off) | 0 | Equivalence partitioning | TS_DHSWL_578
b) To check the DHSWL behaviour while Autarky appeared during Proveout Time
| SRS ID | Precondition |  | Input |  | Output |  | Test Strategy | SRTP ID | Remarks
|  | ECU mode | Voltage Condition | IGN Condition | Power Cut off | Timing DHS_RILReq since IGNON till 6s+/-0.15s | Timing DHS_RILReq after 6s+/-0.15s till ECU off
| SRS_DHSWL_157 | ITM | Normal Voltage (12V) | IGN On and wait for 3s - 5.850s | Yes | 1 | 0 | Equivalence partitioning | TS_DHSWL_667
|  |  |  | IGN On and wait for 6s - 8s | Yes | 1 | 0 | Equivalence partitioning
|  |  |  | IGN On and wait for 2s | Yes | $1 from IGNON till power off. | Stop CAN transmission | Equivalence partitioning
|  |  | Low Voltage (7V) | IGN On and wait for 3s - 5.850s | Yes | 1 | 0 | Equivalence partitioning | TS_DHSWL_668
|  |  |  | IGN On and wait for 6s - 8s | Yes | 1 | 0 | Equivalence partitioning
|  |  |  | IGN On and wait for 2s | Yes | $1 from IGNON till power off. | Stop CAN transmission | Equivalence partitioning
|  |  | High Voltage (16.5 V) | IGN On and wait for 3s - 5.850s | Yes | 1 | 0 | Equivalence partitioning | TS_DHSWL_669
|  |  |  | IGN On and wait for 6s - 8s | Yes | 1 | 0 | Equivalence partitioning
|  |  |  | IGN On and wait for 2s | Yes | $1 from IGNON till power off. | Stop CAN transmission | Equivalence partitioning
c) To check the WIM when fault is qualified/ dequalified in autarky time
| SRS ID | Precondition |  | Input |  |  | Output |  | Test Strategy | SRTP ID | Remarks
|  | ECU mode | Voltage Condition | faulty condition (1) | Time of IGN off after faulty condition (1) | Timing | Fault State (in same POC of (1) in autarky time) | DHS_RILReq until ECU off
| SRS_DHSWL_157 | Normal mode | Normal mode (12V) | Create fault condition: rb_psem_OpenLinePCS1D_flt | 2100 ms | Autarky Time (450 ms) | Qualified | 0 | Equivalence partitioning | TS_DHSWL_675
|  |  |  | Remove fault condition: rb_psem_OpenLinePCS1P_flt | 4200 ms | Autarky Time (450 ms) | Dequalified | 3 | Equivalence partitioning
|  |  | Low voltage (7V) | Create fault condition: rb_psem_OpenLinePCS2D_flt | 2100 ms | Autarky Time (450 ms) | Qualified | 0 | Equivalence partitioning | TS_DHSWL_676
|  |  |  | Remove fault condition: rb_psem_OpenLinePCS2P_flt | 4200 ms | Autarky Time (450 ms) | Dequalified | 3 | Equivalence partitioning
|  |  | High Voltage (20V) | Create fault condition: rb_psem_OpenLinePCS3D_flt | 2100 ms | Autarky Time (450 ms) | Qualified | 0 | Equivalence partitioning | TS_DHSWL_677
|  |  |  | Remove fault condition: rb_psem_OpenLinePCS3P_flt | 4200 ms | Autarky Time (450 ms) | Dequalified | 3 | Equivalence partitioning
The power is cut off before the fault dequalified
(The fault qualified/ dequalified during Autarky time)
NOTE: The time of IGN cut off will depend on the qualification, dequalification time of the fault cause tolerance is 10%
d) To check the WIM when faulty condition is created during autarky time
| SRS ID | Precondition |  | Input |  |  | Output |  | Test Strategy | SRTP ID | Remarks
|  | ECU mode | Voltage Condition | IGN Off | Faulty condition | Timing | Fault State (in autarky time) | DHS_RILReq during autarky
| SRS_DHSWL_157 | Normal mode | Normal mode (12V) | Yes | Create fault condition: rb_psem_OpenLinePCS1D_flt | Autarky Time (450 ms) | No Qualified | 0 | Equivalence partitioning | TS_DHSWL_683
[5 empty] | Remove fault condition: rb_psem_OpenLinePCS1P_flt | Autarky Time (450 ms) | No Dequalified | 3 | Equivalence partitioning
|  |  | Low voltage (7V) |  | Create fault condition: rb_psem_OpenLinePCS2D_flt | Autarky Time (450 ms) | No Qualified | 0 | Equivalence partitioning | TS_DHSWL_684
[5 empty] | Remove fault condition: rb_psem_OpenLinePCS2P_flt | Autarky Time (450 ms) | No Dequalified | 3 | Equivalence partitioning
|  |  | High Voltage (20V) |  | Create fault condition: rb_psem_OpenLinePCS3D_flt | Autarky Time (450 ms) | No Qualified | 0 | Equivalence partitioning | TS_DHSWL_685
[5 empty] | Remove fault condition: rb_psem_OpenLinePCS3P_flt | Autarky Time (450 ms) | No Dequalified | 3 | Equivalence partitioning
SRS_FL_MazdaFaultList_AB12 version 0.11

## 5.NotOperationFault
DHS Warning Lamp Not Operation Fault |  |  |  | (DTC: 0x80D301)
Confirmation point:
Check DSHWL Not Operation Fault in different conditions.
Conditions considered:
1. Abnormal Voltage
2. Bus-off condition
Voltage Dependency:
1. Set Voltage as 12V
2. Set Abnormal Voltage
Testing Technique:
1. Equivalence partitioning
a) To check [DHS Warning Lamp Not Operation Fault] qualified
| SRS_ID | Precondition |  |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times
| SRS_DHSWL_197 | Not qualified | Presenet->No | < 10V in last 10ms (Abnormal Voltage) | 3 | 10 | Not Qualified | 881-884
| SRS_DHSWL_285 |  | No | < 10V in last 10ms (Abnormal Voltage) -> >10V in last 1.5s (Normal Voltage) |  |  | Not Qualified | 881-884
| SRS_DHSWL_198 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | Not Qualified | 711 712 713 714
[6 empty] | 10 | Qualified
b) To check [DHS Warning Lamp Not Operation Fault] re-qualified
| SRS_ID | Precondition |  |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times
| SRS_DHSWL_198 | Fault present in system with bit [test failed = 0] | No | >10V in last 1.5s (Normal Voltage) | 3 | 10 | Qualified
c)To check [DHS Warning Lamp Not Operation Fault] pending with DHS_RIL_STAT not received
| SRS_ID | Precondition |  |  | Input |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times | Value | Times
| SRS_DHSWL_200 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | Not Send (2s) | 0 | Not Qualified | 703
| SRS_ID | Precondition |  |  | Input |  | Input |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times | Value | Times | Value | Times
| SRS_DHSWL_200 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | Not Send | 0 | 3 | 1 | Qualified | 703
d) To check [DHS Warning Lamp Not Operational Fault] reset with value of DHS_RIL_STAT other than $3
| SRS_ID | Precondition |  |  | Input |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times | Value | Times
| SRS_DHSWL_287 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | 0 | 1 | Not Qualified | 720
[7 empty] | 1 |  |  | 721
[7 empty] | 2 |  |  | 722
[7 empty] | 4 |  |  | 723
[7 empty] | 5 |  |  | 724
[7 empty] | 6 |  |  | 725
[7 empty] | 7 |  |  | 726
| SRS_ID | Precondition |  |  | Input |  | Input |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times | Value | Times | Value | Times
| SRS_DHSWL_287 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | 0 | 1 | 3 | 1 | Not Qualified | Covered by TC below
1
2
4
5
6
7
|  | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | 0 | 1 | 3 | 10 | Qualified | 720
[7 empty] | 1 |  |  |  |  | 721
[7 empty] | 2 |  |  |  |  | 722
[7 empty] | 4 |  |  |  |  | 723
[7 empty] | 5 |  |  |  |  | 724
[7 empty] | 6 |  |  |  |  | 725
[7 empty] | 7 |  |  |  |  | 726
e) To check [DHS Warning Lamp Not Operational Fault] reset with Abnormal Voltage
| SRS_ID | Precondition |  |  | Input |  |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Voltage condition | Fault
[5 empty] | Value | Times
| SRS_DHSWL_221 | Not qualified | No | >10V in last 1.5s (Normal Voltage | 3 | 9 | < 10V in last 10ms (Abnormal Voltage) | Not Qualified | 702
| SRS_ID | Precondition |  |  | Input | [7 empty] | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times |  | Value | Times |  | Value | Times
| SRS_DHSWL_221 | Not qualified | No | >10V in last 1.5s (Normal Voltage | 3 | 9 | < 10V in last 10ms (Abnormal Voltage) | 3 | 1 | >10V in last 1.5s (Normal Voltage | 3 | 1 | Not Qualified | 702
[12 empty] | 10 | Qualified
f) To check [DHS Warning Lamp Not Operational Fault] reset with BUS OFF condition
| SRS_ID | Precondition |  |  | Input |  |  |  |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | BUS OFF | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times |  | Value | Times
| SRS_DHSWL_223 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | Present (2s) | 3 | 1 | Not Qualified | 701
| SRS_ID | Precondition |  |  | Input |  | Input |  |  | Input |  |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | BUS OFF | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | BUS OFF | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times |  | Value | Times |  | Value | Times
| SRS_DHSWL_223 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 9 | Present (2s) | 3 | 1 | No | 3 | 1 | Not Qualified | 701
[12 empty] | 10 | Qualified
g) To check [DHS Warning Lamp Not Operational Fault] disqualified with voltage condition
| SRS_ID | Precondition |  |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times
| SRS_DHSWL_227 | Qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 1 | Disqualified | 732
[5 empty] | 1 |  |  | 733
[5 empty] | 2 |  |  | 734
[5 empty] | 3 | 10 | Not Disqualified | 735
[5 empty] | 4 |  |  | 736
[5 empty] | 5 |  |  | 737
[5 empty] | 6 |  |  | 738
[5 empty] | 7 |  |  | 739
|  |  |  | < 10V in last 10ms (Abnormal Voltage) | 0 | 1 | Disqualified | 744
[5 empty] | 1 |  |  | 745
[5 empty] | 2 |  |  | 746
[5 empty] | 3 | 10 | Not Disqualified | Covered by TC 735-738
4
5
6
7
h) To check DHS Warning Lamp Not Operational Fault disqualified and pending with not receive DHS_RIL_STAT
| SRS_ID | Precondition |  |  | Input |  | Output | TS tag | Remark
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times
| SRS_DHSWL_200 | Qualified | No | >10V in last 1.5s (Normal Voltage) | Not Send (2s) | 0 | Not Disqualified | 753 | (1)Observe the fault at the time fault qualified (2)Observe the fault after fault qualified (1s)
< 10V in last 10ms (Abnormal Voltage)
i) To check [DHS Warning Lamp Not Operational Fault] disqualified and pending with bus off present
| SRS_ID | Precondition |  |  | Input |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times
| SRS_DHSWL_200 | Qualified | Present | >10V in last 1.5s (Normal Voltage) | 1 | 10 | Not Disqualified | 752
< 10V in last 10ms (Abnormal Voltage)
j) To check [DHS Warning Lamp Not Operational Fault] behaviour with ECU reset
| SRS_ID | Precondition |  |  | Input |  |  |  | Output | TS tag
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Reset ECU 5 times | Reset Type | Fault
[5 empty] | Value | Times
| SRS_DHSWL_227 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 5 | Yes | Hard Reset/ Soft Reset/ Customer diganostic | Not Qualified | 760-763
| SRS_ID | Precondition |  |  | Input | [5 empty] | Output | TS tag | Remark
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Reset ECU 5 times | Reset Type | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Times |  |  | Value | Times
| SRS_DHSWL_227 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 5 | Yes | Hard Reset/ Soft Reset/ Customer diganostic | 3 | 10 | Qualified | 764-767 | Observe the fault at the time fault qualified
| SRS_ID | Precondition |  |  | Input |  |  |  | Output | TS tag | Remark
|  | DHS Warning Lamp Not Operational Fault | BUS OFF | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Reset ECU 5 times | Reset Type | Fault
[5 empty] | Value | Times
| SRS_DHSWL_227 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 3 | 10 | Yes | Hard Reset/ Soft Reset/ Customer diganostic | Qualified | 764-767 | Reset ECU at the time fault qualified

## 6.MisMatch Fault
DHS Warning Lamp MisMatch Fault (DTC: 0x80D329)
Confirmation point:
Check DSHWL MisMatch Fault in different conditions.
Conditions considered:
1. Abnormal Voltage
2. Bus-off condition
Voltage Dependency:
1. Set Voltage as 12V
2. Set Abnormal Voltage
Testing Technique:
1. Equivalence partitioning
a) To check [DHS Warning Lamp Mismatch Fault] qualify
SRS_ID | Precondition |  |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | Codition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[6 empty] | Value | Times
SRS_DHSWL_299 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | After 6s from IGN on | 0 | 1 | 10 | Qualified | 772
[6 empty] | 2 |  |  | 773
[6 empty] | 4 |  |  | 774
[6 empty] | 6 |  |  | 775
[6 empty] | 7 |  |  | 776
SRS_DHSWL_298 |  |  |  | During 6s after IG On | $1 | 0 |  |  | 777
[6 empty] | 2 |  |  | 778
[6 empty] | 4 |  |  | 779
[6 empty] | 6 |  |  | 780
[6 empty] | 7 |  |  | 781
SRS_DHSWL_297 |  |  |  | 2 Mazda plant mode after proveout time | 2 | 0 |  |  | 782
[6 empty] | 1 |  |  | 783
[6 empty] | 4 |  |  | 784
[6 empty] | 6 |  |  | 785
[6 empty] | 7 |  |  | 786
SRS_DHSWL_296 |  |  |  | 3 DHS Warning Lamp Fault | 3 | 0 |  |  | 787
[6 empty] | 2 |  |  | 788
[6 empty] | 4 |  |  | 789
[6 empty] | 6 |  |  | 790
[6 empty] | 7 |  |  | 791
SRS_ID | Precondition |  |  |  |  | Input |  | Output | Remark | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | Codition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[6 empty] | Value | Times
SRS_DHSWL_242 | Not qualified | No | < 10V in last 10ms (Abnormal Voltage) | After 6s from IGN on | 0 | 1 | 10 | Not Qualified |  | Covered by tc 810-813
|  |  |  | During 6s after IG On | $1 | 0
|  |  |  | Mazda plant mode after proveout time | 2 | 0
|  |  |  | DHS Warning Lamp Fault | 3 | 0
SRS_DHSWL_241 |  |  | < 10V in last 10ms (Abnormal Voltage) -> >10V in last 1.5s (Normal Voltage) | After 6s from IGN on | 0 | 1 | 10 | Not Qualified
|  |  |  | During 6s after IG On | $1 | 0
|  |  |  | Mazda plant mode after proveout time | 2 | 0
|  |  |  | DHS Warning Lamp Fault | 3 | 0
SRS_DHSWL_254 |  |  | >10V in last 1.5s (Normal Voltage) | After 6s from IGN on | 0 | 1 | 10 | Qualified | Cover by other Test Case in above table
|  |  |  | During 6s after IG On | $1 | 0
|  |  |  | Mazda plant mode after proveout time | 2 | 0
|  |  |  | DHS Warning Lamp Fault | 3 | 0
SRS_ID | Precondition |  |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | Codition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[6 empty] | Value | Times
SRS_DHSWL_254 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | After proveout time | 0 | 1 | 10 | Qualified
[5 empty] | $1 | 0
[5 empty] | 2 | 0
[5 empty] | 3 | 0
SRS_ID | Precondition |  |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | Codition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[6 empty] | Value | Times
SRS_DHSWL_254 | Fault present in system with bit [test failed = 0] | No | >10V in last 1.5s (Normal Voltage) | After proveout time | 0 | 1 | 10 | Qualified
[5 empty] | $1 | 0
[5 empty] | 2 | 0
[5 empty] | 3 | 0
b) To check [DHS Warning Lamp Mismatch Fault] re-qualify
SRS_ID | Precondition |  |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | Codition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[6 empty] | Value | Times
SRS_DHSWL_254 | Fault present in system with bit [test failed = 0] | No | >10V in last 1.5s (Normal Voltage) | After 6s from IGN on | 0 | 1 | 10 | Qualified | 861
|  |  |  | During 6s after IG On | $1 | 0 |  |  | 862
|  |  |  | Mazda plant mode after proveout time | 2 | 0 |  |  | 863
|  |  |  | DHS Warning Lamp Fault | 3 | 0 |  |  | 864
c) To check [DHS Warning Lamp Mismatch Fault] reset with no mismatch condition
SRS_ID | Precondition |  |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | IGN On | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
[5 empty] | Value | Value | Times
SRS_DHSWL_317 | Not qualified | On | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | Not Qualified | 797
[5 empty] | 1 |  |  |  | 798
[5 empty] | 2 |  |  |  | 799
[5 empty] | 3 |  |  |  | 800
SRS_ID | Precondition |  |  |  | Input |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times | Value | Times
SRS_DHSWL_270 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | 0 | 1 | Not Qualified | 797
|  |  |  | 1 |  |  | 1 |  |  | 798
|  |  |  | 2 |  |  | 2 |  |  | 799
|  |  |  | 3 |  |  | 3 |  |  | 800
SRS_ID | Precondition |  |  |  | Input |  | Input |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times | Value | Times | Value | Times
SRS_DHSWL_270 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | 0 | 1 | 6 | 1 | Not Qualified | 797
|  |  |  | 1 |  |  | 1 |  | 2 |  |  | 798
|  |  |  | 2 |  |  | 2 |  | 3 |  |  | 799
|  |  |  | 3 |  |  | 3 |  | 0 |  |  | 800
| Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | 0 | 1 | 1 | 10 | Qualified | 797
|  |  |  | 1 |  |  | 1 |  | 2 |  |  | 798
|  |  |  | 2 |  |  | 2 |  | 3 |  |  | 799
|  |  |  | 3 |  |  | 3 |  | 0 |  |  | 800
d) To check [DHS Warning Lamp Mismatch Fault] reset with bus off present
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_301 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 4 | 9 | Not Qualified | 820
|  |  |  | 1 |  |  |  | 821
|  |  |  | 2 |  |  |  | 822
|  |  |  | 3 |  |  |  | 823
SRS_ID | Precondition |  |  |  | Input |  |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | BUS OFF | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_301 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 4 | 9 | Present (2s) | Not Qualified | 820
|  |  |  | 1 |  |  |  |  | 821
|  |  |  | 2 |  |  |  |  | 822
|  |  |  | 3 |  |  |  |  | 823
SRS_ID | Precondition |  |  |  | Input | [5 empty] | Output | Remark | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | BUS OFF | BUS OFF | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times |  |  | Value | Times
SRS_DHSWL_301 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 4 | 9 | Present (2s) | No | 6 | 1 | Not Qualified | Fault is check after Busoff recovery | 820
|  |  |  | 1 | [8 empty] | 821
|  |  |  | 2 | [8 empty] | 822
|  |  |  | 3 | [8 empty] | 823
|  |  |  | 0 |  |  |  |  | 6 | 10 | Qualified |  | 820
|  |  |  | 1 | [8 empty] | 821
|  |  |  | 2 | [8 empty] | 822
|  |  |  | 3 | [8 empty] | 823
e) To check [DHS Warning Lamp Mismatch Fault] reset with voltage condition
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_301 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | Not Qualified | 810
|  |  |  | 1 | 6 |  |  | 811
|  |  |  | 2 | 7 |  |  | 812
|  |  |  | 3 | 7 |  |  | 813
SRS_ID | Precondition |  |  |  | Input |  |  |  |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times |  | Value | Times
SRS_DHSWL_301 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | < 10V in last 10ms (Abnormal Voltage) | 4 | 10 | Not Qualified | 810
|  |  |  | 1 | 6 | 9 |  | 2 |  |  | 811
|  |  |  | 2 | 7 | 9 |  | 0 |  |  | 812
|  |  |  | 3 | 7 | 9 |  | 7 |  |  | 813
SRS_ID | Precondition |  |  |  | Input | [7 empty] | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Voltage condition | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times |  | Value | Times |  | Value | Times
SRS_DHSWL_301 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | < 10V in last 10ms (Abnormal Voltage) | 4 | 1 | >10V in last 1.5s (Normal Voltage) | 6 | 1 | Not Qualified | 810
|  |  |  | 1 | 6 |  |  | 2 |  |  | 6 |  |  | 811
|  |  |  | 2 | 7 |  |  | 0 |  |  | 6 |  |  | 812
|  |  |  | 3 | 7 |  |  | 7 |  |  | 7 |  |  | 813
|  |  | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 |  | 4 | 1 |  | 6 | 10 | Qualified | 810
|  |  |  | 1 | 6 |  |  | 2 |  |  | 6 |  |  | 811
|  |  |  | 2 | 7 |  |  | 0 |  |  | 6 |  |  | 812
|  |  |  | 3 | 7 |  |  | 7 |  |  | 7 |  |  | 813
f) To check [DHS Warning Lamp Mismatch Fault] pendding with value of DHS_RIL_STAT is $3
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | Not Qualified | 801
|  |  |  | 1 | 6 |  |  | 802
|  |  |  | 2 | 7 |  |  | 803
|  |  |  | 3 | 7 |  |  | 804
SRS_ID | Precondition |  |  |  | Input |  |  |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times | Value | Times
SRS_DHSWL_278 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | 3 | 1 | Not Qualified | 801
|  |  |  | 1 | 6 |  |  |  |  | 802
|  |  |  | 2 | 7 |  |  |  |  | 803
|  |  |  | 3 | 7 |  |  |  |  | 804
SRS_ID | Precondition |  |  |  | Input | [5 empty] | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times | Value | Times | Value | Times
SRS_DHSWL_278 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | 3 | 1 | 6 | 1 | Qualified | 801
|  |  |  | 1 | 6 |  |  |  | 6 | 1 |  | 802
|  |  |  | 2 | 7 |  |  |  | 7 | 1 |  | 803
|  |  |  | 3 | 7 |  |  |  | 7 | 1 |  | 804
g) To check [DHS Warning Lamp Mismatch Fault] pendding with not receive DHS_RIL_STAT
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | Not Qualified | 824
|  |  |  | 1 | 6 |  |  | 825
|  |  |  | 2 | 7 |  |  | 826
|  |  |  | 3 | 7 |  |  | 827
SRS_ID | Precondition |  |  |  | Input |  |  |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | Not receive |  | Not Qualified | 824
|  |  |  | 1 | 6 |  |  |  |  | 825
|  |  |  | 2 | 7 |  |  |  |  | 826
|  |  |  | 3 | 7 |  |  |  |  | 827
SRS_ID | Precondition |  |  |  | Input | [5 empty] | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times |  |  | Value | Times
SRS_DHSWL_278 | Not qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 6 | 9 | Not receive |  | 0 | 1 | Qualified | 824
|  |  |  | 1 | 6 |  |  |  | 6 |  |  | 825
|  |  |  | 2 | 7 |  |  |  | 4 |  |  | 826
|  |  |  | 3 | 7 |  |  |  | 2 |  |  | 827
h) To check DHS Warning Lamp Mismatch Fault disqualify
SRS_ID | Precondition |  |  |  | Input |  | Output | Remark | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_294 | Qualified | No | >10V in last 1.5s (Normal Voltage) | 0 | 0 | 1 | Disqualified | Cover by testcase below
|  |  |  | 0 | 5
SRS_DHSWL_293 |  |  |  | 1 | 1
|  |  |  | 1 | 5
SRS_DHSWL_292 |  |  |  | 2 | 2
|  |  |  | 2 | 5
SRS_DHSWL_291 |  |  |  | 3 | 1
|  |  |  | 3 | 5
SRS_DHSWL_294 | Qualified | No | < 10V in last 10ms (Abnormal Voltage) | 0 | 0 | 1 | Disqualified |  | 833
|  |  |  | 0 | 5 |  |  |  | 834
SRS_DHSWL_293 |  |  |  | 1 | 1 |  |  |  | 835
|  |  |  | 1 | 5 |  |  |  | 836
SRS_DHSWL_292 |  |  |  | 2 | 2 |  |  |  | 837
|  |  |  | 2 | 5 |  |  |  | 838
SRS_DHSWL_291 |  |  |  | 3 | 1 |  |  |  | 839
|  |  |  | 3 | 5 |  |  |  | 840
i) To check DHS Warning Lamp Mismatch Fault disqualify and pending with value of DHS_RIL_STAT is 3
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Qualified | No | >10V in last 1.5s (Normal Voltage) | Don't Care | 3 | 10 | Not Disqualified | 854
|  |  | < 10V in last 10ms (Abnormal Voltage) |  |  |  |  | 854
j) To check DHS Warning Lamp Mismatch Fault disqualify and pending with not receive DHS_RIL_STAT
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Qualified | No | >10V in last 1.5s (Normal Voltage) | Don't Care | Not send | Not send | Not Disqualified | 847
|  |  | < 10V in last 10ms (Abnormal Voltage) |  |  |  |  | 847
k) To check DHS Warning Lamp Mismatch Fault disqualify and pending with bus off present
SRS_ID | Precondition |  |  |  | Input |  | Output | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Qualified | Present | >10V in last 1.5s (Normal Voltage) | Don't Care | Don't Care | Don't Care | Not Disqualified | 846
|  |  | < 10V in last 10ms (Abnormal Voltage) |  |  |  |  | 846
l) To check DHS Warning Lamp Mismatch Fault qualify and disqualify with ECU reset
SRS_ID | Precondition |  |  |  | Input | [5 empty] | Output | Remark | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Reset ECU 5 times | Reset Type | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Fault
|  |  |  | Value | Value | Times |  |  | Value | Times
SRS_DHSWL_278 | Note Qualified | No | >10V in last 1.5s (Normal Voltage) | Don't Care | 6 | 5 | Yes | Hard Reset/ Soft Reset/ Customer diganostic | 6 | 10 | Not Qualified | Check fault after proveout time | 870-872
SRS_ID | Precondition |  |  |  | Input |  |  |  | Output | Remark | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Reset ECU 5 times | Reset Type | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Note Qualified | No | >10V in last 1.5s (Normal Voltage) | Don't Care | 6 | 5 | Yes | Hard Reset/ Soft Reset/ Customer diganostic | Not Qualified | Check fault after proveout time | 873-875
SRS_ID | Precondition | [5 empty] | Input |  | Output | Remark | TS tag
| DHS Warning Lamp Mismatch Fault | BUS OFF | Voltage condition | DHS_RIL_REQ (Send from SAS ECU To HEC) | DHS_RIL_STAT (Send from HEC to SAS ECU) |  | Reset ECU 5 times | Reset Type | Fault
|  |  |  | Value | Value | Times
SRS_DHSWL_278 | Note Qualified | No | >10V in last 1.5s (Normal Voltage) | Don't Care | 6 | 10 | Yes | Hard Reset/ Soft Reset/ Customer diganostic | Qualified | Check fault after proveout time | 873-875